## Revision Block
System Safety/Security Certifiable Items List (CIL)
Revisions
No. | Date | Description | ORIG | CHKR | Contractor Approval | Agency Approval
0 | 2012-10-04 | Base Line Draft | BCC

## CIL Template
[6 empty] | Safety/Security Certifiable Items list Rev: Baseline Draft Date: | Design Conformance Checklist |  |  | Installation & Construction Conformance Checklist |  |  | Testing & Inspection Conformance Checklist |  |  | Final Verification |  |  | Certifiable Items List Template Concurrence:
Level 1 - Element | Level 2 - Sub-Element | Level 3 - Item | Level 4 - Sub (1) | level 5 - Sub (2) Item | Item Description | Design Criteria | Doc Ref | Verified By | Date | Doc Ref | Verified By | Date | Doc Ref | Verified By | Date | Doc Ref | Verified By | Date | Comments
1 | 0 |  |  |  | Facilities
1 | 1 |  |  |  | Facilities - General
1 | 1 | 1 |  |  | Provide a copy of the Fairfax County Certificate of occupancy for the appropriate phase of the garage.
1 | 1 | 2 |  |  | Provide a copy of the final certification letter prepared by the Special Inspections Engineer of record and submitted to Fairfax County documenting successful testing and inspection of soil placement & compaction
1 | 1 |  |  |  | Facilities - Construction
1 | 1 | 1 |  |  | Grading, Excavating & Backfilling
1 | 1 | 1 | 1 |  | Provide final certification letter from geotechnical engineer of record that the last 12" of backfill under WMATA structural foundations is compacted to 100% | Approved Construction Documents | NA | NA
1 | 1 | 1 | 2 |  | Provide final certification letter from geotechnical engineer of record that the last 12" of backfill under WMATA maintained utilities is compacted to 100% | Approved Construction Documents | NA | NA
1 | 1 | 2 |  |  | Caissons
1 | 1 | 2 | 1 |  | Provide final certification letter and reports from geotechnical engineer of record for caisson bearing. | Approved Construction Documents | NA | NA
1 | 1 | 2 | 2 |  | Copy of the final certification letter from SIER and submitted to Fairfax County documenting successful testing and inspection of Caissons. | Approved Construction Documents | NA | NA
1 | 1 | 3 |  |  | Cast In Place Concrete
1 | 1 | 3 | 1 |  | Provide final certification from SIER / 3rd party testing agancy for all CIP concrete placement as follows: | Approved Construction Documents | NA | NA
1 | 1 | 3 | 1 | 1 | Soil Bearing Test Reports | Approved Construction Documents | NA | NA
1 | 1 | 3 | 1 | 2 | Rebar Inspection Reports | Approved Construction Documents | NA | NA
1 | 1 | 3 | 1 | 3 | Concrete Compressive strength tests | Approved Construction Documents | NA | NA
1 | 2 |  |  |  | Facilities - Precast Concrete
1 | 2 | 1 |  |  | Verify horizontal surfaces of stair treds have slip resistant finish | Approved Construction Documents | 03410-2.12.A.7
1 | 2 | 2 |  |  | Provide final certification letter from precast concrete testing lab, sealed by the designer of the precast, certifying all precast was tested and inspected in accordance with PCI MNL 116 section 6.2 and has complied with requirements of ACI 318 - 2008. Further that all precast erected is capable of meeting design loads. | Approved Construction Documents | 03410-2.13.B & C
1 | 2 | 3 |  |  | Verify walking surfaces have a slip resistant finish | Approved Construction Documents | 03410-3.3.D.4
1 | 2 | 4 |  |  | Verify chain link inserts are installed at all lite / shear wall openings where indicated on approved plans. | Approved Construction Documents | Precast sheet EKP and Submittal | NA
1 | 3 |  |  |  | Facilities - Misc. Metals
1 | 3 | 1 |  |  | Verify structural steel (Canopy &bus Shelters) supports at the vent shaft have been installed in accordance with construction documents. | Approved Construction Documents | S-121 | N/A
1 | 3 | 4 |  |  | Misc. Metals - Fencing
1 | 3 | 4 | 1 |  | Verify the installation of metal fencing and gate on the G-6 level of stair-A, separating level G-6 from G-7 Elevator Machine Room | Approved Construction Documents | Detail 3 / A-210 and Detail 1 / A-211
1 | 3 | 4 | 2 |  | Verify that chain link fence is installed in the B-2 Level between air shaft and B-2 parking as per Walker Parking plans. | Approved Construction Documents | Detail 1 / S-311
1 | 3 | 4 | 3 |  | Verify Chain Link fence and gate are installed in the B-2 Level storage area (B2-04) adjacent to the WMATA and Retail Switchgear rooms. | Approved Construction Documents | Detail 1 / A-201 &
1 | 3 | 5 |  |  | Misc. Metals - Hand Railings
[5 empty] | Verify Hot Dipped Galvanized, non-painted Metals |  | N/A | N/A
1 | 3 | 5 | 4 |  | Verify the railing on top of the precast garage, Phase-1, on the North elevation is installed as per plan. | Approved Construction Documents | Detail 6 & 8 / A-501 | N/A
1 | 4 |  |  |  | Facilities - Fireproofing
1 | 4 | 1 |  |  | Test and inspect spray fire proofing in accord with VAUSBC 2003 section 1704.11. Location is in the Police & Security Office. | Approved Construction Documents | 07810-3.04.A.1
1 | 4 | 2 |  |  | Provide certification letter from Special Inspections Engineer of Record that spray fireproofing has successfully passed testing and inspection requirements in item 151 above and a minimum 3/4" thickness was achieved. | Approved Construction Documents | 07810-3.04.A.D
1 | 4 | 3 |  |  | Verify all deck penetrations have been adequately smoke sealed with a system of a single manufacturer designed to achieve a flame spread of less than 25 and a smoke generation of less than 450 as per ASTM E-84 | Approved Construction Documents | 07841-1.02.C
1 | 5 |  |  |  | Facilities - Fire Protection
1 | 5 | 1 |  |  | Site & Underground
1 | 5 | 1 | 1 |  | Confirm that a temporary Fire Hydrant (or permanent Hydrant in Bus Loop) is installed and acceptable to the Fire Marshal with respect to FDC location | Approved Construction Documents | Civil Sheet 11 of 88 | N/A | [10 empty] | This is a phase 2 item
1 | 5 | 1 | 2 |  | Confirm 6" fire water pipe are run from the Water room to the B-2 WMATA water room. | Approved Construction Documents | F-100, PL-202 & PL-203 | N/A | [10 empty] | Per the most current Plumbing drawings, there will be an 8" fire water pipe from outside directly to the Fire Protection Room.
1 | 5 | 1 | 3 |  | Provide water leak test at 125 psig for 24 hours | Approved Construction Documents | 02515-3.19.2.e
1 | 5 | 1 | 4 |  | Provide pressure test at 175 psig for 1-hour on Ductile Iron UG Pipe | Approved Construction Documents | 02515-3.19.2.g.2)
1 | 5 | 1 | 5 |  | Flush 6" UG fire mains at 750 GPM and 8" fire mains at 1000 GPM prior to connecting to back flow preventors. | Approved Construction Documents | 13905-3.10.D
1 | 5 | 1 | 6 |  | Provide copy of the fire main flush certificate whitnessed by Fire Marshal and Building Inspector. | Approved Construction Documents | 13905-1.03.B.3
1 | 6 |  |  |  | Facilities - Grounding & Bondiing |  | E-300
1 | 6 | 2 |  |  | Man holes & Hand Holes
1 | 6 | 2 | 1 |  | Ground Metalic Manholes and Hand Holes & Lids | Approved Construction Documents | 16060-3.01.G.3, E-300
1 | 6 | 2 | 2 |  | Test Manhole / Handhole grounding for continuity (no minimum ohms specified) | Approved Construction Documents | 16060-3.03, E-300
1 | 6 | 3 |  |  | Ground & Bond Precast Lite Wall chain link fence inserts with #6 AWG conductor and test continuity to ground. | Approved Construction Documents | K7-E-300
1 | 6 | 4 |  |  | Structural Steel for Vent Shaft - No Bonding Required for these elements as they are not accessible | Approved Construction Documents | K7-E-300
1 | 6 | 5 |  |  | Traction Elevator Grounding
1 | 6 | 5 | 2 |  | Ground metal stair and handrails at G-7 elevator machine room at the top of stair A vestibule with #6 AWG conductor to local bus bar and test continuity to ground. | Approved Construction Documents | 16060-3.01.G.3 & 16060-3.03.B, E-300
1 | 6 | 5 | 4 |  | Bond WMATA Traction elevator guide rails via #1/0 awg conductor to local elevator bus connected to AC switchboard room bus | Approved Construction Documents | 16060-3.01.G.2 E-300
1 | 6 | 7 |  |  | Ground & Bond Stair-A metal fencing on the south wall, level G-1 through G-5 with #6 AWG conductor and test continuity to ground. | Approved Construction Documents | 16060-3.01.G.3
1 | 6 | 8 |  |  | Ground & Bond B-2 chain link fence between air shaft and parking with #6 AWG conductor and test continuity to ground. | Approved Construction Documents | K7-E-300 & 16060-3.03.B
1 | 6 | 9 |  |  | Ground & Bond B-2 chain link fence in storage area between switchgear rooms with #6 AWG conductor and test continuity to ground. | Approved Construction Documents | K7-E-300 & 16060-3.03.B
1 | 6 | 10 |  |  | Stair A & B Grounding
1 | 6 | 10 | 1 |  | Ground and Bond stair A handrails with #6 AWG Conductor and test continuity to ground. | Approved Construction Documents
1 | 6 | 10 | 2 |  | Ground and Bond stair B handrails with #6 AWG Conductor and test continuity to ground. | Approved Construction Documents
1 | 6 | 10 | 3 |  | Ground & Bond Stair-A metal fencing on the south wall, level G-1 through G-5 with #6 AWG conductor and test continuity to ground. | Approved Construction Documents
1 | 6 | 11 |  |  | Verify the railing on top of the precast garage, Phase-1 north is grounded and bonded with #6 AWG Conductor. Test continuity. | Approved Construction Documents
1 | 6 | 12 |  |  | Ground & Bond site handrail at Transit Road / Western Array with separate ground rod and #6 AWG conductor. Test continuity of Bonding (if required) and continuity to ground. | Approved Construction Documents
1 | 6 | 13 |  |  | Verify Ground and bonding of the following doors and frames with a #6 AWG conductor to the local bus within the room and test for continuity to ground. | Approved Construction Documents
1 | 6 | 13 | 2 |  | WMATA AC Switchgear Room (excludes Retail Switchgear Room)
Light poles and lighting
1 | 6 | 13 | 3 |  | Doors
1 | 6 | 15 | 1 |  | Verify ground of Signal Bridge. | Approved Construction Documents
1 | 6 | 15 | 2 |  | Verify ground of Remote Lot Full Sign. | Approved Construction Documents
1 | 6 | 15 | 3 |  | Verify ground of Card Reader . | Approved Construction Documents
1 | 6 | 15 | 4 |  | Verify ground of Gate Console. | Approved Construction Documents
1 | 6 | 15 | 5 |  | Verify ground of Array Booth and Control Equipment Cabinet. | Approved Construction Documents
1 | 6 | 15 | 6 |  | Verify ground of Load Center in Array Booth. | Approved Construction Documents
1 | 6 | 16 |  |  | Fire Sprinkler Piping
1 | 6 | 16 | 1 |  | Verify #2 AWG bonding strap installed at all mechanical joints | Approved Construction Documents
1 | 6 | 16 | 2 |  | Test electrical continuity of bonded joints on Sprinkler piping with total resistance not to exceed calculated resistance value of bond cable by 10%. | Approved Construction Documents
1 | 6 | 17 |  |  | Grounding - Misc
1 | 6 | 17 | 1 |  | Provide certified Reports verifying ground resistance of each grid and each bus do not exceed specified values. | Approved Construction Documents
1 | 6 | 17 | 2 |  | Verify Grounding Installed as follows:
1 | 6 | 17 | 2 | 1 | One grounding electrode to out door Dominion Va Power Transformer for WMATA garage, from nearest ground grid | Approved Construction Documents
1 | 6 | 17 | 2 | 2 | Ground Grid in WMATA Switchgear Room with 3.-6" minimum #4 / 0 AWG grounding electrode above finished slab connected to Bus installed in room. Test ground resistance not to exceed 2-ohms | Approved Construction Documents
1 | 6 | 17 | 2 | 3 | Test Ground Resistance of Bus in each electric closet on floors B-1 through G-6 not to exceed 5-ohms | Approved Construction Documents
1 | 6 | 17 | 2 | 4 | Verify ground bus in communications closet's on floors B-1 through G-6 is connected via #2/0 AWG ground conductor back to the AC switchboard ground grid. Test ground resistance not to exceed 5-ohms. | Approved Construction Documents
1 | 6 | 17 | 2 | 6 | Ground each site light pole to a separate 5/8" ground rod using a #6 AWG ground conductor. Test continuity to ground. | Approved Construction Documents
1 | 6 | 17 | 2 | 7 | Ground each light pole on top tier of garage to garage ground grid using a #6 AWG ground conductor. Test continuity to ground. | Approved Construction Documents
1 | 6 | 17 | 2 | 8 | Ground Bus Supervisor shelter to separate ground grid using #6 AWG ground conductor | Approved Construction Documents
1 | 6 | 17 | 2 | 9 | Ground 2-separate Bus Shelter columns / posts to 2-separate ground rods with #6 AWG conductor. Test continuity to ground. | Approved Construction Documents
1 | 6 | 17 | 2 | 10 | Ground Station Entrance Pylon separate 5/8" ground rod using #6 AWG ground conductor. Test continuity to ground | Approved Construction Documents
1 | 6 | 17 | 2 | 11 | Ground Metal Railing around Bus Loop that separates passengers from bus traffic using a separate 5/8" ground rod and a #6 AWG ground conductor. Test continuity to ground | Approved Construction Documents
1 | 6 | 18 |  |  | Switchgear Grounding
1 | 6 | 18 | 1 |  | Test continuity to ground of AC switchboard enclosure, Main Distribution Panels | Approved Construction Documents
1 | 6 | 18 | 2 |  | Confirm that bus installed in AC switchboard room is grounded to a grid with a #4/0 AWG conductor.
1 | 8 | 1 | 5 |  | Verify operation of the passenger - Kiosk communications as follows: | Approved Construction Documents
1 | 9 |  |  |  | Facilities - Signage
1 | 12 | 3 | 3
1 | 14 |  |  |  | NOT USED
1 | 10 |  |  |  | Facilities - Access/Egress
1 | 10 | 3 |  |  | PARCS | Approved Construction Documents
1 | 10 | 3 | 1 |  | Test Insulation Resistance to Ground. | Approved Construction Documents
1 | 10 | 3 | 2 |  | Test Insulation Resistance of each bus section in the Array Load Center. | Approved Construction Documents
1 | 10 | 3 | 3 |  | Demonstration of PARCS Equipment done to ensure they work properly
1 | 10 | 3 | 3 | 1 | Demonstrate that all lanes and each gate function properly | Approved Construction Documents
1 | 10 | 3 | 3 | 2 | Demonstrate an automatic system failure mode for gates showing gates open on power failure. | Approved Construction Documents
1 | 10 | 3 | 3 | 3 | Demonstrate Remote Control of Gates from 600 5th Street Central PARCs control center. | Approved Construction Documents
1 | 10 | 3 | 3 | 4 | Demonstrate Credit Card Reader and peripherials are functioning correctly | Approved Construction Documents
1 | 10 | 3 | 3 | 5 | Demonstrate Remote control function from 600 5th Street for Credit Card Reader and peripherials. | Approved Construction Documents
1 | 10 | 3 | 3 | 6 | Demonstrate operation of mini UPS system in each array booth during transfer of power to the emergency generator. | Approved Construction Documents
1 | 10 | 3 | 3 | 7 | Demonstrate operation of mini UPS system in each array booth to to have a 1-hour capacity | Approved Construction Documents
1 | 10 | 3 | 3 | 8 | Demonstrate lane traffic control signals | Approved Construction Documents
1 | 13 |  |  |  | Facilities - Electrical
1 | 13 | 3 |  |  | Low Voltage Switchgear | Approved Construction Documents
1 | 13 | 3 | 1 |  | Confirm Switchgear is tied to the AEMS system | Approved Construction Documents
1 | 13 | 4 |  |  | Circuit Brakers, Load Centers & Panel Boards | Approved Construction Documents
1 | 13 | 4 | 1 |  | Test molded case circuit breakers from pole to pole and pole to ground using a 1,000 volt megger with insulation resistance to be 50 megohms minimum. Provide test report. | Approved Construction Documents
1 | 13 | 4 | 2 |  | Test each bus section phase-to phase and phase-to -ground for one minute using 1,000 volt megger with resistance to be not less than 2-megohms or manufacturers recommendation. | Approved Construction Documents
1 | 13 | 4 | 3 |  | Test all enclosures for continuity to ground | Approved Construction Documents
1 | 13 | 4 | 4 |  | Check and adjust magnetic trips to be as per the approved coordination study. | Approved Construction Documents
1 | 13 | 5 |  |  | Lighting Fixtures & Mounting Poles | Approved Construction Documents
1 | 13 | 5 | 1 |  | Test all lighting circuits for operation | Approved Construction Documents
1 | 13 | 5 | 2 |  | Test light poles and poles for continuity to ground. | Approved Construction Documents
1 | 13 | 6 |  |  | Automated Energy Management System (AEMS) | Approved Construction Documents
1 | 13 | 6 | 1 |  | Verify the following equipment is connected to the AEMS system and is subject to testing. | Approved Construction Documents
1 | 13 | 6 | 1 | 1 | Garage Lighting (monitor and control)
1 | 13 | 6 | 1 | 2 | Bus Loop Lighting
1 | 13 | 6 | 1 | 3 | Emergency Generator (monitor run, start & off)
1 | 13 | 6 | 1 | 4 | Fuel Tank & Fill (monitor level)
1 | 13 | 6 | 1 | 5 | Elevators (monitor power consumption; kiosk monitoring is performed under the elevator section)
1 | 13 | 6 | 1 | 6 | Retail Sump Pump (Monitor run, stop, alarm)
1 | 13 | 6 | 1 | 7 | Elevator Sump Pump
1 | 13 | 6 | 1 | 8 | B-2 Retail Ventilation Fans and AHU (monitor run, stop, alarm)
1 | 13 | 6 | 1 | 9 | Sewage Ejector Pump (run, stop, alarm)
1 | 13 | 6 | 2 |  | Perform the following tests:
1 | 13 | 6 | 2 | 1 | Perform Polarity and continuity testing for all AEMS connected equipment | Approved Construction Documents
1 | 13 | 6 | 2 | 2 | Perform start up of each Remote Terminal Unit (RTU) | Approved Construction Documents
1 | 13 | 6 | 2 | 3 | Verify Control & Monitoring points in accord with Table-1 and 2 | Approved Construction Documents
2 |  |  |  |  | Communications
3 | 0 |  |  |  | Training
3 | 1 |  |  |  | PARCS
3 | 5 |  |  |  | Plumbing Systems
3 | 5 | 1 |  |  | Drainage Pumping System
3 | 7 |  |  |  | Electrical
3 | 7 | 1 |  |  | Wiring and Control Devices
3 | 7 | 3 |  |  | Switchgear
3 | 7 | 4 |  |  | AEMS System
3 | 8 |  |  |  | Communications
3 | 8 | 1 |  |  | GETS
4 | 0 |  |  |  | Documentation
4 | 1 |  |  |  | Drilled Concrete Piers | Approved Construction Documents
4 | 1 | 1 |  |  | As-Builts | Approved Construction Documents
4 | 2 |  |  |  | Underground Electrical and Communication Distribution Systems | Approved Construction Documents
4 | 2 | 1 |  |  | As-Builts | Approved Construction Documents
4 | 3 |  |  |  | PARCS | Approved Construction Documents
4 | 3 | 1 |  |  | Operation and Maintenance Manuals | Approved Construction Documents
3 | 29 | 5 |  |  | Certification | 11101-1.4.F.6
4 | 4 |  |  |  | Fire Protection and Alarm | Approved Construction Documents
4 | 4 | 1 |  |  | Operation and Maintenance Manuals | Approved Construction Documents
4 | 9 |  |  |  | Air Conditioning | Approved Construction Documents
4 | 9 | 1 |  |  | Operation and Maintenance Manuals | Approved Construction Documents
4 | 10 |  |  |  | Heating Equipment | Approved Construction Documents
4 | 10 | 1 |  |  | Operation and Maintenance Manuals | Approved Construction Documents
4 | 12 |  |  |  | Control Equipment | Approved Construction Documents
4 | 12 | 1 |  |  | Operation and Maintenance Manuals | Approved Construction Documents
4 | 14 |  |  |  | Motors | Approved Construction Documents
4 | 14 | 1 |  |  | Operation and Maintenance Manuals | Approved Construction Documents
4 | 15 |  |  |  | Transformers | Approved Construction Documents
4 | 15 | 1 |  |  | Operation and Maintenance Manuals | Approved Construction Documents
4 | 16 |  |  |  | Motor Starters and Control Centers | Approved Construction Documents
4 | 16 | 1 |  |  | Operation and Maintenance Manuals | Approved Construction Documents
4 | 17 |  |  |  | Low-Voltage Switchgear | Approved Construction Documents
4 | 17 | 1 |  |  | Operation and Maintenance Manuals | Approved Construction Documents
4 | 18 |  |  |  | AEMS | Approved Construction Documents
4 | 18 | 1 |  |  | Operation and Maintenance Manuals | Approved Construction Documents
4 | 19 |  |  |  | Communication Systems in Parking Structure | Approved Construction Documents
4 | 19 | 1 |  |  | Operation and Maintenance Manuals | Approved Construction Documents
4 | 20 |  |  |  | FINALS
4 | 20 | 1 |  |  | Provide a copy of the Fairfax County Certificate of occupancy for the appropriate phase of the garage.
4 | 20 | 2 |  |  | Provide a copy of the final certification letter prepared by the Special Inspections Engineer of record and submitted to Fairfax County documenting successful testing and inspection of soil placement & compaction
Comments
[18 empty] | Verified By |  |  | Date | MC Special Inspection Sign Off
[18 empty] | MO. CO. |  | WMATA SAFE
Compressive Strength Test Results, slump, air content and concrete temperature.
To include documentation from engineer of record for acceptance of failed CSL tests.
As Builts performed by surveyor licensed in the state of Maryland.
Engineer of record acceptance of Balter reports for competent rock.
Plain and Epoxy Coated
Plain and Epoxy Coated
Compressive Strength Test Results, slump, air content and concrete temperature.
Replaced Secant Pile Wall

## Initials Legend
Design |  |  |  |  | Construction / Installation |  |  |  |  | Startup / Testing
Initial | Discipline | First Name | Last Name | Company/Office | Initial | Discipline | First Name | Last Name | Company/Office | Initial | Discipline | First Name | Last Name | Company/Office
[5 empty] | BCC | Contractor | Clark | Campbell | MCRT
CIL Configuration Management
Initial | Discipline | First Name | Last Name | Company/Office
KK | SS | Kevin | Kuebler | PB/WMATA/SAFE
RLF | SS | Richard | Fasy | PB/WMATA/SAFE

## ABB
Abbreviations: |  | Discipline Codes
ADAAG | American Disabilities | A - Architectural
AHJ | Authority Having Jurisdiction | B - Bridges and Aerial
AORA | Area Of Rescue Assistance | C - Civil (Grading, Drainage and ROW)
ASCE | American Society of Civil Engineers | E - Electrical
ATC | Automatic Train Control | F - Communications
CCTV | Closed Circuit Television | G - Geotechnical
COMM | Communication | J - Train Control
DGS | Department of General Services | M - Mechanical
DSCP | Design Standard Change Proposal | P - Traction Power
ETEC | Emergency Transportation and Evacuation Cart | R - Track and Alignment
fc | Foot-candles | S - Structural
FIA | Fire & Intrusion Alarm system | T - Civil (Traffic and Roadway)
FLS | Fire Life Safety | U - Civil (Utilities)
HVAC | Heating, Ventilation, and Air Conditioning | Z - Engineering Management
IAW | In Accordance With | SS - System Safety
IBC | International Building Code
IDS | Intrusion Detection System
IDW | Intrusion Detection Warning
LAN | Local Area Network
NEC | National Electrical Code
NFPA | National Fire Protection Association
OCC | Operation Control Center
OSHA | Occupation Safety Health Association
PA | Public Address
PIDS | Passenger Information Display System
SCADA | Supervisory Control and Data Acquisition
SCWG | Safety/Security Certification Working Group
SIER | Special Inspections Engineer of Record
SPEC | Specification
TBD | To Be Determined
UPS | Uninterruptable Power Supply
WAN | Wide Area Network
WMATA | Washington Metropolitan Area Transportation Authority